[PROJECT NAME]

[DATE DD/MM/YY]

Date

RIBA Stage [DESIGN STAGE] Fire Strategy Report

www.firedynamicsgroup.com

Fire Dynamics Group

[CLIENT]

Client

Version History

| Revision | Description | Date | Author | Checked by |
| --- | --- | --- | --- | --- |
| 00 | First Issue, for comment | [DATE DD/MM/YY] | [AUTHOR] |  |

Fire Dynamics

WeWork Aldwych House

71-91 Aldwych

WC2B 4HN

UK

Fire Dynamics Group Ltd 13476929

This document is confidential and for the exclusive benefit of the client. It may not be assigned to or relied upon by a third party without the agreement of the client. However, this strategy report may be used by the end user of the building in the development of any fire safety management procedures and plans considered necessary to fulfil their responsibilities under applicable fire safety legislation.

[AUTHOR FIRST NAME]@firedynamicsgroup.com

- Table of Contents

1.	Introduction	4

2.	Project Overview	6

2.1.	Site Description	6

2.2.	Building Description	6

3.	Fire Safety Design Approach	8

3.1.	Design Guidance	8

3.2.	Fire Safety Management	8

3.3.	The Regulatory Reform (Fire Safety) Order 2005	8

3.4.	Regulation 38	8

3.5.	The Construction (Design and Management) Regulations 2015	8

3.6.	Materials and Workmanship	9

3.7.	Property Protection	9

4.	Fire Alarm and Detection Systems	10

4.1.	Evacuation Strategy	10

4.2.	System Category / Type	10

4.3.	Design and Installation of Systems	10

5.	Horizontal Means of Escape	11

5.1.	Maximum Travel Distances	11

5.2.	Number of Exit Routes	11

5.3.	Widths of Escape Routes and Exits	11

5.4.	Maximum Horizontal Exit Capacities	12

5.5.	Door Swings and Door Heights	12

5.6.	Enclosure of Corridors that are not Protected Corridors	12

5.7.	Sub-Division of Corridors	12

5.8.	Inner Rooms and Access Rooms	13

5.9.	Height of Escape Routes	13

5.10.	Minimum Dimensions of Corridors	13

5.11.	Means of Escape from the Roof	13

5.12.	Emergency Lighting and Signage	13

5.13.	Access Control and Direction of Door Openings	13

5.14.	Power Supplies to Fire Safety Systems	13

6.	Vertical Means of Escape	14

6.1.	Stair Capacity	14

6.2.	Access Lobbies and Corridors	14

6.3.	Disabled Refuges	14

6.4.	Final Exits from Stairs	14

6.5.	Reception Area	14

7.	Internal Fire Spread (Linings)	16

7.1.	Internal Surfaces	16

8.	Internal Fire Spread (Structure)	17

8.1.	Loadbearing Elements of Structure	17

8.2.	Compartmentation	17

8.3.	Fire Doors (All Areas)	17

8.4.	Cavity Barriers	17

8.5.	Pipework	18

8.6.	Ventilation Ducts and Flues	18

9.	External Fire Spread	19

9.1.	Space Separation	19

9.2.	Construction of External Walls and Roofs	20

10.	Firefighting Provisions	21

10.1.	Perimeter Access	21

10.2.	Fire Hydrant Provision	21

11.	References	22

Appendix A - Fire Strategy Drawings	23

Appendix B - Fire Hydrant Schematic	24

Introduction

Fire Dynamics has been appointed by [CLIENT] to provide fire safety engineering advice for the proposed [PROJECT NAME] development in [PROJECT LOCATION]. This report covers the base build development only, the fit out will be subject to a further Building Regulations submission prior to occupation.

    - The main objectives of this report are to:

Provide fire safety advice using the guidance given in Approved Document B: Volume 2 (AD-B)[1];

Highlight areas of the design that deviate from the guidance in this document;

Provide detailed calculations/justifications in support of any alternative fire engineering approaches that have been used to provide a comparable level of fire safety to that implied by the measures in Approved Document B.

    - The design approach outlined in this report will ensure that the highest level of staff and visitor fire safety is attained whilst ensuring that operational requirements and architectural aspirations are met.

    - All information contained in the report should be read in conjunction with the architectural general arrangement drawings, the information provided in the appendices and all other supporting documentation prepared and submitted by other consultants who are acting on behalf of the design team.

Project Overview

  - Building Description

The building…. [USER TO COMPLETE THIS]

Figure 1: Site Plan Showing the Location and Scale of the Development

- Fire Safety Design Approach

  - Design Guidance

    - In relation to fire safety, the building is required to meet the functional requirements of Part B of the Building Regulations 2010[2]. The fire strategy has been developed using the guidance given in Approved Document B: Volume 2.

    - Whilst the framework in AD-B permits numerous trade-offs in active and passive fire safety measures, it is not a perfect tool meaning some redundancy in design may still arise when its methods are used. In these cases, alternative fire safety engineering techniques using the framework outlined in BS 7974[3] can be used. This mixing of design approach is permitted in AD-B, provided the designer or engineer has a thorough understanding of the relevant fire safety issues and takes sufficient care when developing such an integrated approach.

    - Where not explicitly stated within this report it is assumed that, in all aspects, the building will be designed to comply with the relevant sections of Approved Document B and other supporting documentation.

  - Fire Safety Management

    - The 2017 version of BS 9999[3] specifies two levels of fire safety management that could be followed.  Level 1 is an enhanced level of management which conforms to a management system standard such as PAS 7[4]. Level 2 is an adequate level of management that satisfies the minimum requirements of legislation. Given that the fire strategy for this building is not particularly complex when compared to other buildings of this size / use, it is our view that a management level of “2” is sufficient for this building. It is recommended that the end user reviews the management considerations outlined in Section 8 of BS 9999.

  - The Regulatory Reform (Fire Safety) Order 2005

    - The operation of the common and communal areas of the building will be subject to The Regulatory Reform (Fire Safety) Order 2005[5], (FSO).

    - Under the FSO, the Responsible Person must carry out an assessment of the risks stemming from the possibility of fire in the premises, and must implement fire precautions where necessary and to the extent that is reasonable and practicable to control those risks.

    - On occupation of the building, or part thereof, the ‘responsible person’ as defined in the FSO is required by law to undertake a ‘suitable and sufficient’ fire risk assessment. This fire safety strategy will not satisfy this obligation. Instead, it should be used as a basis for understanding the fire safety provisions provided in the building in order to undertake the risk assessment. The fire risk assessment will help identify risks that can be removed or reduced and to decide the nature and extent of the general fire precautions that need to be taken to protect people against the fire risks that remain. It should pay particular attention to those at special risk, such as the disabled and those with special needs, and must include consideration of any dangerous substance likely to be on the premises.

  - Regulation 38

    - Regulation 38 of The Building Regulations requires the fire safety information to be given to the Responsible Person (as defined in the FSO) at the completion of the project or when the building or extension is first occupied. As a minimum it will be necessary for the occupier of the building to be given this fire safety strategy, all “as built” fire strategy plans and all information relating to the fire safety systems within the building.

  - The Construction (Design and Management) Regulations 2015

    - The Construction (Design and Management) Regulations 2015 (CDM)[6] are applicable to the design and construction stages of this project. These regulations are intended to focus attention on planning and management throughout construction projects, from design stage and onwards. The aim is for health and safety considerations to be treated as an essential, but normal part of a project's development - not an afterthought or bolt-on extra.

    - Such matters do not specifically form part of this fire safety strategy. However, where our role on the project involves the preparation or modification of designs, this will be undertaken in conjunction with the project’s principal designer and CDM Coordinator to ensure that any foreseeable risks during construction and the maintenance and use of the building are sufficiently controlled. These risks will typically be summarised in the principal designer’s or principal contractor’s risk register.

  - Materials and Workmanship

    - It is assumed that all building work will be carried out in accordance with Regulation 7 of the Building Regulations. Therefore, to ensure that the proposed fire safety systems detailed within this report achieve the appropriate fire performance, it is crucial that all products, components, materials or structures relating to the fire strategy are installed using competent companies/people and, where applicable, third party accreditation/certification is provided.

  - Property Protection

    - The main aim of the report is to demonstrate how the buildings proposed package of fire safety measures will ensure compliance is achieved with the Functional Requirements in Part B (Fire Safety) of the Building Regulations 2010. The objective of the functional requirements detailed in Part B of the Building Regulations 2010 is to protect against the loss of life only. As such, measures to prevent property, content and business losses are not explicitly considered in the report.

- Fire Alarm and Detection Systems

  - Evacuation Strategy

    - All occupants within the building will evacuate simultaneously upon activation of the fire alarm.

  - System Category / Type

    - When fitted out, there will be a landlord’s requirement for all areas to be provided with a minimum of a category [ALARM CATEGORY] fire alarm and detection system in accordance with BS 5839-1[7]. It should be noted that this category of fire detection and alarm system exceeds the minimum requirements for the office. The minimum level is a manual (M) system.

    - As a minimum, the warehouse will be provided with suitable infrastructure to allow the installation of the fire detection and alarm system but automatic fire detection will not be installed at this stage, with all areas being provided with a manual fire alarm system only at base build stage. This is considered reasonable given that the warehouse will not be occupied until after it is fitted out.

    - A category [ALARM CATEGORY] fire alarm and detection system in accordance with BS 5839-1[7] will be provided to all areas of the building. It should be noted that this category of fire detection and alarm system exceeds the minimum requirements for the office. The minimum level is a manual (M) system.

    - Audible coverage should be provided to the roof. As an alternative, visual beacons could be provided adjacent to the escape routes with any occupants on the roof provided with pagers to alert them of a fire.

  - Design and Installation of Systems

    - Upon installation of the fire detection and alarm system an installation and commission certificate should be obtained.

- Horizontal Means of Escape

  - Maximum Travel Distances

    - The applicable travel distances for all areas of the building are provided in Table 2. These distances have been taken from Table 2.1 of AD-B.

| Use | Purpose Group | Maximum Travel Distance When Escape is Provided in: |  |
| --- | --- | --- | --- |
|  |  | One Direction Only (m) | Alternative Directions (m) |
| Warehouse | 6 | 25 | 45 |
| Office | 3 | 18 | 45 |
| Plant Areas | 2-7 | 18 | 45 |

Table 1: Summary of Recommended Travel Distances

    - The travel distances in Table 2 are currently met with the proposed base build layouts. It is noted that these distances will need to be reassessed as part of the internal fit out works when the internal layouts of the space are known. These works will be subject to a separate Building Regulations application. Should the internal layout cause travel distances to exceed the limits above, a fire engineering assessment will need to be undertaken to prove the suitability of the proposed layouts.

    - The travel distances in Table 2 are met throughout the design.

    - The warehouse has multi-directional travel distances which exceed those suggested in Table 2 (maximum direct distance of approximately [MAXIMUM TRAVEL DISTANCE]m) with the shell and core layout, which will likely increase when the fit out of the building is completed). This is typically resolved using a fire engineering study, most likely involving a computational fluid dynamics (CFD), to determine whether occupants can safely escape should fire occur. However, the results of such a study would be influenced by the layout of the space and the volume of the warehouse which is occupied by obstructions (i.e. racking). At this base build stage, the actual layout is unknown so this assessment cannot be meaningfully completed. However, a fire engineering assessment will need to be conducted at the fit out stage to assess whether the actual travel distances are appropriate for the proposed layout, or if additional fire protection measures are needed.

    - The fire engineering study will need to compare the Available Safe Egress Time (ASET) with the Required Safe Egress Time (RSET). It is anticipated that the results will show that there is a significant margin of time available between ASET and RSET within the warehouse and, as such, the increase in travel distances can be considered reasonable given the large volume of the space and the associated time taken for smoke to fill down and affect conditions at Ground Floor level.

    - The warehouse has multi-directional travel distances which exceed those suggested in Table 2 (maximum direct distance of approximately [MAXIMUM TRAVEL DISTANCE]m). AD-B provides limits on multi-directional travel distances to ensure that all occupants can leave the building before a smoke layer can “fill-down” and affect multiple escape routes simultaneously.

    - However, the time taken for this to occur is dependent on the fire growth rate, the fire protection measures installed and the volume of the space to fill. In this warehouse, significantly greater travel distances to those permitted in Table 2.1 of AD-B can be justified. This is based on a combination of the large volume of the space, relatively low population and the large number of fire exits, which means prolonged evacuation times, created as a result of queuing at final exit points, are unlikely.

    - To assess the ability of occupants to escape safely from the warehouse, a Computational Fluid Dynamics (CFD) study has been undertaken. This analysis calculates the speed at which a rising smoke plume will reach the underside of the roof and then descend towards designated fire exits at the lower level of the warehouse. The necessity for CFD is driven by the need to determine whether the smoke layer will descend to lower levels before reaching the outer boundaries of the enclosing space. The early descent of a smoke layer sometimes occurs in large open spaces due to significant heat losses between the smoke layer and outer enclosure, which reduces the buoyancy of the smoke.

    - The study compares the Available Safe Egress Time (ASET) with the Required Safe Egress Time (RSET).  The results show that there is a significant margin of time available between ASET and RSET within the warehouse and, as such, the increase in travel distances can be considered acceptable.

  - Number of Exit Routes

    - In accordance with the guidance given in Table 2.2 of AD-B, the minimum number of escape routes should be determined by the number of persons using them. In this building the following number of escape routes will be provided to rooms, areas and storeys with the following occupancies:

Up to 60 persons – at least one escape route;

60 – 600 persons – at least two escape routes; and

More than 600 persons – at least three escape routes.

  - Widths of Escape Routes and Exits

    - The minimum recommended widths for escape routes and exits are provided in Table 3. These values have been taken from Table 2.3 of AD-B.

| Maximum Number of People | Minimum Width1 (mm) |
| --- | --- |
| 60 | 750 |
| 110 | 850 |
| 220 | 1050 |
| More than 220 | 5 per person2 |

Table 2: Minimum Exit Width Requirements

Notes

1. Widths may need to be increased to meet Approved Document M recommendations.

2. This factor does not apply to an opening serving fewer than 220 persons.

  - Maximum Horizontal Exit Capacities

    - Based on the figures detailed above, the maximum number of occupants per area are provided in Table 4. In the absence of specific occupancy numbers, the total occupancy per area has been calculated on the basis of floor space factors within Table D1 in AD-B.

| Area / Level | Number / Width of Exits2 | Maximum Exit Capacity | Floor Space Factor | Estimated Occupancy4 |
| --- | --- | --- | --- | --- |
| Warehouse1 (7,432m2) | 7×1000mm, 1×1650mm | 770 persons | 30m2/person | 248 persons |
| Plant Area | 1×850mm | 60 persons |  | 12 persons |
| Main Office Ground Floor (Meeting Room) | 1×1900mm (i)3 | 60 persons | 6m2/person | 15 persons |
| Main Office First Floor (Open Plan Office) | 1×1200mm5 | 60 persons |  | 53 persons |

Table 3: Recommended and Expected Horizontal Exit Capacities

Notes

1. The areas are GIAs and do not account for the space occupied by racking/machinery at fit out, which is a conservative assumption in this case.

2. Approximate dimensions, to be confirmed by the design team. Where more than one exit is available, the largest exit is discounted.

3. (i) indicates an inwardly-opening door.

4. Some of the occupants are double-counted, which is a conservative assumption.

5. Although there are two 1600mm wide doors at this level, the single stair is taken as the limiting factor for the exit capacity from this floor, as a conservative assumption.

    - The table shows that the maximum recommended occupancies are greater than the estimated occupancies in all areas. The end user should be made aware of these maximum capacities and ensure that they are not exceeded.

  - Door Swings and Door Heights

    - As stated in Section 5.11 of AD-B, all doors on escape routes should be hung to swing in the direction of escape where they are intended to serve more than 60 people.

  - Enclosure of Corridors that are not Protected Corridors

    - In accordance with paragraph 2.25 in AD-B, all corridors that form part of an escape route but are not protected corridors should be constructed out of smoke retarding construction and enclosed with full height partitions that finish either at the underside of the structural floor above or at a suspended ceiling.

  - Sub-Division of Corridors

    - In accordance with paragraph 2.26 in AD-B, corridors which connect two final exits that are 12m or greater apart will be provided with a cross corridor door. These doors should be FD20S standard or higher and be provided with 0.1m2 vision panels.

    - The width of a door which subdivides a corridor should be not less than 1050mm, or the calculated corridor width minus 150mm, whichever is the greater. If the area is inaccessible for wheelchair users then the door can be a minimum 800mm wide, otherwise a minimum door width of 850mm should be provided.

  - Inner Rooms and Access Rooms

    - Access rooms are rooms through which occupants must escape to leave the building. In accordance with Section 2.11 in AD-B, all access rooms in this scheme should be provided with an automatic fire detection and alarm system. The guidance states that inner rooms should not house more than 60 persons and access rooms should not be a place of ‘special fire hazard’.

  - Height of Escape Routes

    - In accordance with Section 5.16 in AD-B, all escape routes (except for door frames) should be provided with a minimum clear height of 2m.

  - Minimum Dimensions of Corridors

    - All escape corridors will be a minimum 1.2m wide, or 1m if inaccessible for wheelchair users.

  - Means of Escape from the Roof

    - Besides PV panels, no other equipment is to be provided on the roof, and roof access will be infrequent and for maintenance purposes only. Nonetheless, it is a requirement of the occupier to ensure that maintaining the roof can be achieved safely so adequate means of escape will be designed into the building.

    - The roof is provided with two permanent means of escape via a roof access hatch on the north side which discharges onto the plant deck below and another cat ladder on the south side. The maximum travel distance from any part of the roof to one of the escape routes would be less than the 100m limit recommended in Table 2.1 in AD-B. As such, this arrangement is considered reasonable.

  - Emergency Lighting and Signage

    - Emergency lighting will be provided in all escape routes in accordance with BS 5266-1:2016[8]. Signage should be provided as per BS 5499-4:2013[9] and BS ISO 3864-1:2011[10].

  - Access Control and Direction of Door Openings

    - Any doors located on escape routes that are normally secured against entry should only be fitted with a lock or fastening which is readily operated, without the use of a key and without having to manipulate more than one mechanism.

    - Where the door is likely to be used by more than 60 persons, panic hardware complying with BS EN 1125[11] should be installed on the side approached by persons making their escape. Any electrically powered locks will need to return to the unlocked position on operation of the fire alarm system, on loss of power, or on operation of a manual door release unit positioned on the side approached by people making their escape.

  - Power Supplies to Fire Safety Systems

    - The cables for any electrical circuits associated with equipment required to function during a fire will be suitably robust and their routes carefully chosen to limit the potential for damage to those cables. Secondary power supplies will be required to all equipment required to function during a fire, such as the fire detection and alarm system and sprinkler systems. The emergency lighting system back-up power supply will consist of individual batteries.

    - Where possible, all insulation and sheathing on cables should be of the zero-halogen low smoke (0HLS) type to minimise the risk from toxic and corrosive fumes and smoke.

- Vertical Means of Escape

  - Stair Capacity

    - The stair capacity has been calculated based on the capacities in Table 3.2 in AD-B.

    - The upper storey of the main Office Building and the plant deck are accessed via one protected 1200mm wide stair. The capacity of a 1200mm wide stair serving two storeys is 285 persons. This exceeds the estimated overall occupancy for the office and plant deck levels – 65 persons.

  - Access Lobbies and Corridors

    - As per Section 3.34 in AD-B, as the stair is the only one serving the plant deck and upper office level, it should be provided with lobby protection on the lower levels, i.e. into the office on First Floor and meeting room at Ground Floor (a lobby is provided to the warehouse at Ground Floor and on the plant deck). However, the proposed layout is considered reasonable on the following basis, subject to discussion and agreement with the Statutory Authorities:

The plant deck will be accessed infrequently for maintenance only, by trained members of staff.

Occupants in the open plan office on First Floor will have to travel only one level within the stair and the stair is provided with a lobby to the warehouse at Ground Floor, which arguably can contain a greater fire hazard, compared to an office.

Both levels below the plant deck have large open volumes. Consequently, the probability of smoke accumulating and pushing through the stair door affecting the stair before occupants on the upper levels escaped is low.

  - Disabled Refuges

    - A clear space (refuge area) greater than 900mm x 1400mm should be provided within each stair at each level where an area where no level egress routes are available.

    - Each refuge area should be provided with an appropriate two-way communication device complying with BS 5839-9[12] consisting of Type B outstations which communicate with a master station located adjacent to the main fire alarm panel.

  - Final Exits from Stairs

    - As per Section 2.23 in AD-B, the final exit from the stair is required to be sized to accommodate both the occupants of the upper levels descending the stair and the occupants escaping via the stair at Ground Floor level. This is calculated using the following formula:

- W =(N/2.5+60×S)/80

- where:

- W  = The required width of the final exit (m)

- N = The number of people served by the exit at Ground (51)

- S = The width of the stair (1.2m)

    - On this basis, the required final exit width is 1,155mm. The actual width of the final exit is approximately 1900mm.

  - Reception Area

    - A reception lobby with an area of approximately 45m2 is provided within the stair at Ground Floor level. As stairs are recommended to be maintained as sterile spaces, at this is the only stair serving the upper levels, it is recommended that any furniture installed in this area is non-combustible and management procedures will be in place to ensure that no fuel loading is stored here. Any future fit out proposal will be subject to a further Building Regulations submission. As part of the fit out design, the design team should be cognisant that the enclosure of the stair should be kept sterile as it is the only stair serving the upper office levels.

- Internal Fire Spread (Linings)

  - Internal Surfaces

    - All wall and ceiling linings should meet the relevant classifications given in Table 6.1 of AD-B (extracted in Table 5).

| Location | European Class3 |
| --- | --- |
| Small rooms1 of area not more than 30m2 | D-s3, d2 |
| Other rooms1 | C-s3, d2 |
| Other circulation spaces | B-s3, d2 |

Table 4: Minimum Surface Spread of Flame Classifications

Notes

1. AD-B defines a "room" as "an enclosed space within a building that is not used solely as a circulation space”. The term includes not only conventional rooms, but also cupboards that are not fittings and large spaces such as warehouses and auditoria. The term does not include voids such as ducts, ceiling voids and roof spaces.

2. When a classification includes 's3, d2', this means that there is no limit set for smoke production and/or flaming droplets/particles.

- Internal Fire Spread (Structure)

  - Loadbearing Elements of Structure

    - As the warehouse is contained on a single storey, Table B4 of AD-B states that the required fire resistance period is 60 minutes. In single-storey buildings, elements of structure only require fire resistance if they support a compartment wall or floor. The elements to which this applies are shown in the drawings in Appendix A.

    - The offices are separated from the warehouse by fire resisting compartmentation. All loadbearing elements of structure which support the office areas will be designed to achieve 60 minutes fire resistance.

    - In addition to the above, any structural element which supports a compartment wall will be designed to achieve the period of fire resistance of the wall it supports.

  - Compartmentation

    - As stated in Table 8.1 in AD-B, there is no limit on the size of fire compartments in a single-storey warehouse. For this reason, there is no requirement to divide the building into multiple compartments. Nonetheless, the offices will be separated from the warehouse by construction which achieves at least 60 minutes fire resistance. This separation should include the top roof slab of the offices.

    - Separating elements within the building should be provided with the levels of fire resistance shown in Table 6. These recommendations are as per the guidance given in Tables B3 and B4 in AD-B. Where possible, these requirements are shown graphically in Appendix A.

| Element of Construction | Fire Resistance Period (Minutes) |  |  |
| --- | --- | --- | --- |
|  | Integrity | Insulation | Loadbearing Capacity |
| Loadbearing Elements of Structure | - | - | 60 |
| Loadbearing Elements of Structure Supporting Escape Routes Only | - | - | 30 |
| External Walls Which Require Fire Resistance | 60 | 15 | 60 |
| Walls and Roofs Separating Warehouse from Offices | 60 | 60 | 60 |
| Storage Areas | 30 | 30 | 30 |
| Escape Stairs | 30 | 30 | 60 |
| 1.8m External Separation to Stairs | 30 | 15 | 30 |

Table 5: Compartmentation Requirements

  - Fire Doors (All Areas)

    - All doors that require fire resistance should meet the fire and smoke ratings stated in Table C1 of AD-B.

  - Cavity Barriers

    - Section 9 in AD-B states that cavity barriers should be provided in concealed voids within the building and on the external façade:

- To sub divide the cavity such that no orthogonal dimension exceeds 20m centres;

- Along lines of fire resistance; and

- At the joints of an opening within a wall containing a cavity (i.e. windows and doors).

    - Each cavity barrier should provide 30 minutes fire resistance (integrity only) and 15 minutes insulation and should achieve a UK surface spread of flame classifications of at least Class 1 or corresponding EU classification.

  - Pipework

    - Pipes which pass through fire resisting construction will meet the guidance in Table 31 of BS 9999 (extracted in Table 7).

| Situation | Maximum Nominal Internal Diameter (mm) |  |  |
| --- | --- | --- | --- |
|  | Non-combustible material1 | Lead, aluminium, aluminium alloy, PVC2, fibre-cement | Any other material |
| Structure (but not a wall separating buildings) enclosing a protected shaft which is not a stairway or a lift well | 160 | 110 | 40 |
| Any other situation | 160 | 40 | 404040400 |

Table 6: Maximum Nominal Internal Diameter of Pipes Passing Through Compartmentation

Notes

1. Defined as any material which, if exposed to a temperature of 800°C, will not soften or fracture to the extent that flame or hot gas will pass through the wall of the pipe.

2. uPVC pipes conforming to either BS 4514 or BS 5255.

  - Ventilation Ducts and Flues

    - The integrity of all air handling ducts needs to be maintained when they pass through lines of fire separation.  In this scheme the integrity of these ducts will be maintained using either:

- Fire and, where appropriate, smoke dampers;

- Fire resisting enclosures; or

- Fire resisting ductwork.

    - Motorised fire and smoke dampers are required where an air path exists into and out of an escape route enclosure (e.g. stairs, lobbies and enclosed escape corridors). As a general rule, if the doors through a compartment wall are shown as having smoke seals in Appendix A, any dampers in that wall are required to be motorised. If in doubt, the project fire engineer should be consulted about what type of damper is correct.

- External Fire Spread{% if no_ext_fire_spread_needed %}

    - The proposed works do not affect the external walls of the building. As such, external fire spread provisions should be maintained as per the base build fire strategy. {% else %}

  - Space Separation

    - An external fire spread assessment has been carried out using the enclosing rectangle method detailed in BR 187[13].

    - Using this method, a conservative assumption is made that the entire extent of the façade is located at the same distance from the site boundary as the closest part. A diagram providing the naming conventions for the elevations in this assessment, as well as the assumed boundary distances, is provided in Figure 2.

- [Insert Diagram showing relevant boundaries]

Figure 2: Elevations and Boundary Distances Used in External Fire Spread Assessment

    - The results of the external fire spread assessment are provided in Table 8. {% if t|length == 1 %}

| Boundary Distance (m) | {{t[0][0]}} |
| --- | --- |
| Elevation Width (m) | {{t[0][1]}} |
| Elevation Height (m) | {{t[0][2]}} |
| BRE Width (m) | {{t[0][3]}} |
| BRE Height (m) | {{t[0][4]}} |
| Permitted Unprotected Area | {{t[0][5]}} |
| Permitted Unprotected Area (m2) | {{t[0][6]}} |
| Actual Area of Warehouse Elevation (m2) | {{t[0][7]}} |
| Required Protected Area (m2) | {{t[0][8]}} |
| Required Protected Area (% of Warehouse Elevation) | {{t[0][9]}} |

Table 7: External Fire Spread Assessment (Warehouse) {% elif t|length == 2 %}

| Elevation | 1 | 2 |
| --- | --- | --- |
| Boundary Distance (m) | {{t[0][0]}} | {{t[1][0]}} |
| Elevation Width (m) | {{t[0][1]}} | {{t[1][1]}} |
| Elevation Height (m) | {{t[0][2]}} | {{t[1][2]}} |
| BRE Width (m) | {{t[0][3]}} | {{t[1][3]}} |
| BRE Height (m) | {{t[0][4]}} | {{t[1][4]}} |
| Permitted Unprotected Area | {{t[0][5]}} | {{t[1][5]}} |
| Permitted Unprotected Area (m2) | {{t[0][6]}} | {{t[1][6]}} |
| Actual Area of Warehouse Elevation (m2) | {{t[0][7]}} | {{t[1][7]}} |
| Required Protected Area (m2) | {{t[0][8]}} | {{t[1][8]}} |
| Required Protected Area (% of Warehouse Elevation) | {{t[0][9]}} | {{t[1][9]}} |

Table 8: External Fire Spread Assessment (Warehouse) {% elif t|length == 3 %}

| Elevation | 1 | 2 | 3 |
| --- | --- | --- | --- |
| Boundary Distance (m) | {{t[0][0]}} | {{t[1][0]}} | {{t[2][0]}} |
| Elevation Width (m) | {{t[0][1]}} | {{t[1][1]}} | {{t[2][1]}} |
| Elevation Height (m) | {{t[0][2]}} | {{t[1][2]}} | {{t[2][2]}} |
| BRE Width (m) | {{t[0][3]}} | {{t[1][3]}} | {{t[2][3]}} |
| BRE Height (m) | {{t[0][4]}} | {{t[1][4]}} | {{t[2][4]}} |
| Permitted Unprotected Area | {{t[0][5]}} | {{t[1][5]}} | {{t[2][5]}} |
| Permitted Unprotected Area (m2) | {{t[0][6]}} | {{t[1][6]}} | {{t[2][6]}} |
| Actual Area of Warehouse Elevation (m2) | {{t[0][7]}} | {{t[1][7]}} | {{t[2][7]}} |
| Required Protected Area (m2) | {{t[0][8]}} | {{t[1][8]}} | {{t[2][8]}} |
| Required Protected Area (% of Warehouse Elevation) | {{t[0][9]}} | {{t[1][9]}} | {{t[2][9]}} |

Table 9: External Fire Spread Assessment (Warehouse) {% elif t|length == 4 %}

| Elevation | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| Boundary Distance (m) | {{t[0][0]}} | {{t[1][0]}} | {{t[2][0]}} | {{t[3][0]}} |
| Elevation Width (m) | {{t[0][1]}} | {{t[1][1]}} | {{t[2][1]}} | {{t[3][1]}} |
| Elevation Height (m) | {{t[0][2]}} | {{t[1][2]}} | {{t[2][2]}} | {{t[3][2]}} |
| BRE Width (m) | {{t[0][3]}} | {{t[1][3]}} | {{t[2][3]}} | {{t[3][3]}} |
| BRE Height (m) | {{t[0][4]}} | {{t[1][4]}} | {{t[2][4]}} | {{t[3][4]}} |
| Permitted Unprotected Area | {{t[0][5]}} | {{t[1][5]}} | {{t[2][5]}} | {{t[3][5]}} |
| Permitted Unprotected Area (m2) | {{t[0][6]}} | {{t[1][6]}} | {{t[2][6]}} | {{t[3][6]}} |
| Actual Area of Warehouse Elevation (m2) | {{t[0][7]}} | {{t[1][7]}} | {{t[2][7]}} | {{t[3][7]}} |
| Required Protected Area (m2) | {{t[0][8]}} | {{t[1][8]}} | {{t[2][8]}} | {{t[3][8]}} |
| Required Protected Area (% of Warehouse Elevation) | {{t[0][9]}} | {{t[1][9]}} | {{t[2][9]}} | {{t[3][9]}} |

Table 10: External Fire Spread Assessment (Warehouse) {% elif t|length == 5 %}

| Elevation | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| Boundary Distance (m) | {{t[0][0]}} | {{t[1][0]}} | {{t[2][0]}} | {{t[3][0]}} | {{t[4][0]}} |
| Elevation Width (m) | {{t[0][1]}} | {{t[1][1]}} | {{t[2][1]}} | {{t[3][1]}} | {{t[4][1]}} |
| Elevation Height (m) | {{t[0][2]}} | {{t[1][2]}} | {{t[2][2]}} | {{t[3][2]}} | {{t[4][2]}} |
| BRE Width (m) | {{t[0][3]}} | {{t[1][3]}} | {{t[2][3]}} | {{t[3][3]}} | {{t[4][3]}} |
| BRE Height (m) | {{t[0][4]}} | {{t[1][4]}} | {{t[2][4]}} | {{t[3][4]}} | {{t[4][4]}} |
| Permitted Unprotected Area | {{t[0][5]}} | {{t[1][5]}} | {{t[2][5]}} | {{t[3][5]}} | {{t[4][5]}} |
| Permitted Unprotected Area (m2) | {{t[0][6]}} | {{t[1][6]}} | {{t[2][6]}} | {{t[3][6]}} | {{t[4][6]}} |
| Actual Area of Warehouse Elevation (m2) | {{t[0][7]}} | {{t[1][7]}} | {{t[2][7]}} | {{t[3][7]}} | {{t[4][7]}} |
| Required Protected Area (m2) | {{t[0][8]}} | {{t[1][8]}} | {{t[2][8]}} | {{t[3][8]}} | {{t[4][8]}} |
| Required Protected Area (% of Warehouse Elevation) | {{t[0][9]}} | {{t[1][9]}} | {{t[2][9]}} | {{t[3][9]}} | {{t[4][9]}} |

Table 11: External Fire Spread Assessment (Warehouse) {% elif t|length == 6 %}

| Elevation | 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- | --- |
| Boundary Distance (m) | {{t[0][0]}} | {{t[1][0]}} | {{t[2][0]}} | {{t[3][0]}} | {{t[4][0]}} | {{t[5][0]}} |
| Elevation Width (m) | {{t[0][1]}} | {{t[1][1]}} | {{t[2][1]}} | {{t[3][1]}} | {{t[4][1]}} | {{t[5][1]}} |
| Elevation Height (m) | {{t[0][2]}} | {{t[1][2]}} | {{t[2][2]}} | {{t[3][2]}} | {{t[4][2]}} | {{t[5][2]}} |
| BRE Width (m) | {{t[0][3]}} | {{t[1][3]}} | {{t[2][3]}} | {{t[3][3]}} | {{t[4][3]}} | {{t[5][3]}} |
| BRE Height (m) | {{t[0][4]}} | {{t[1][4]}} | {{t[2][4]}} | {{t[3][4]}} | {{t[4][4]}} | {{t[5][4]}} |
| Permitted Unprotected Area | {{t[0][5]}} | {{t[1][5]}} | {{t[2][5]}} | {{t[3][5]}} | {{t[4][5]}} | {{t[5][5]}} |
| Permitted Unprotected Area (m2) | {{t[0][6]}} | {{t[1][6]}} | {{t[2][6]}} | {{t[3][6]}} | {{t[4][6]}} | {{t[5][6]}} |
| Actual Area of Warehouse Elevation (m2) | {{t[0][7]}} | {{t[1][7]}} | {{t[2][7]}} | {{t[3][7]}} | {{t[4][7]}} | {{t[5][7]}} |
| Required Protected Area (m2) | {{t[0][8]}} | {{t[1][8]}} | {{t[2][8]}} | {{t[3][8]}} | {{t[4][8]}} | {{t[5][8]}} |
| Required Protected Area (% of Warehouse Elevation) | {{t[0][9]}} | {{t[1][9]}} | {{t[2][9]}} | {{t[3][9]}} | {{t[4][9]}} | {{t[5][9]}} |

Table 12: External Fire Spread Assessment (Warehouse)

{% endif %}{% if all_unprotected %}

    - The results of the external fire spread assessment show that there is no requirement for the external walls of the building to be designed to achieve a particular period of fire resistance to prevent external fire spread across the site boundary. {% endif %} {% if has_elevations_protected %}

    - {{ elevations_protected_text }} {% endif %} {% if has_elevations_less_1m %}

    - {{ elevations_less_1m_text }}

Figure 3: Allowable Unprotected Areas for Elevations within 1m of a Boundary (Diagram 13.5 of AD-B) {% endif %}  {% if some_unprotected %}

    - {{ some_unprotected_text }}  {% endif %}

  - Construction of External Walls and Roofs

    - As the top storey height is less than 18m there is no requirement to limit the combustibility of materials used in the construction of the external walls or limit the surface spread of flame classification of the external walls.

    - As the top storey height of the building is greater than 18m, all materials used in the construction of the external walls (including, but not limited to, insulation products, external surfaces, the filler materials of composite panels, structure etc.) should either:

- Meet a European combustibility classification of A2-s3,d2 or better; or

- Meet the performance criteria given in BR 135 for external walls using full scale test data from BS 8414-1 or BS 8414-2.

    - As the height of the building is less than 18m, and boundary distances are greater than 1m, there is no requirement to limit the combustibility of the external surfaces of the building.

    - On elevations [ELEVATIONS within 1m], which are within 1m of the site boundary,

    - Any cavities in the external walls including those filled with insulation should be provided with cavity barriers as per Section 8.4.

    - The allowed combustibility of the materials which form the roof coverings is determined by the nearest distance to the site boundary. In this instance, all roof coverings should achieve a surface spread of flame classification of Croof(t4) (European  Class) or better in accordance with Table 14.1 of AD-B. {% endif %}

- Firefighting Provisions

  - Perimeter Access

    - As suggested in Table 15.1 in AD-B, 15% perimeter access should be provided around the building. Access (doors of minimum 750mm clear width) should be provided so that there is no more than 60m between a door and the end of that façade / another door.

    - Fire Service access roads should have the following clear dimensions and carrying capacities in accordance with Table 15.2 of AD-B:

- Minimum Width Between Kerbs – 3.7m;

- Minimum Width of Gateways – 3.1m;

- Minimum Turning Circle Between Kerbs – 16.8m;

- Minimum turning Circle Between Walls – 19.2m;

- Minimum Clearance Height – 3.7m;

- Minimum Carrying Capacity – 12.5 tonnes.

  - Fire Hydrant Provision

    - A new hydrant system, as per AD-B, will be provided such that hydrants are available within 90m of an entrance to each building and not more than 90m apart. A diagram showing the indicative hydrant locations for the site is provided in Appendix B. This proposed arrangement is as per the guidance in Section 16.9 in AD-B and BS 9990.

    - It is understood that there is a concern that the local water pressure which will supply the hydrant network is insufficient. As such, in order to supplement and increase the reliability of the water flow for the hydrant network, a static tank with a capacity of 45,000L will be provided near the south-eastern corner of Unit 1, as per Section 16.13 of AD-B. This will be a static water tank with suitable hose connections only (i.e. no pumping equipment).

- References

- Approved Document B: Fire Safety Volume 2 – Buildings other than dwellings. 2019 Edition.

- Building Regulations 2010 - Statutory Instrument 2000.  HMSO, 2010.

- BS 9999:2017 - Code of practice for fire safety in the design, construction and use of buildings.

- PAS 7:2013 - Fire risk management system. Specification.

- The Regulatory Reform (Fire Safety) Order 2005 – Statutory Instrument 1541.

- The Construction (Design and Management) Regulations 2015 – Statutory Instrument 51.

- BS 5839-1:2017 - Fire detection and fire alarm systems for buildings - Code of practice for the design, installation, commissioning and maintenance of systems in non-domestic premises.

- BS 5266-1:2016 - Part 1: 2016:  Emergency Lighting. Code of practice for the emergency escape lighting of premises.

- BS 5499-4:2013. Safety signs – Code of practice for escape route signing.

- BS ISO 3864-1:2021 - Graphical symbols - Safety colours and safety signs - Part 1: Design principles for safety signs and safety markings.

- BS EN 1125:2008 - Building hardware. Panic exit devices operated by a horizontal bar, for use on escape routes. Requirements and test methods.

- BS 5839-9:2011 - Fire detection and alarm systems for buildings. Code of practice for the design, installation.

- BR 187 - External fire spread: Building separation and boundary distances. BRE 2014.

Fire Strategy Drawings

Fire Hydrant Schematic